## Collated (2)
Name | Alarm Message | DNP3 Address | Modbus Address | ICS Mapping | EBP Mapping
KOWA01CLOSED | KOW 34.5KV BREAKER 252-1 CLOSED | 0 | 100000 | BKR_A01_CLOSED | BKR_A01_CLOSED
KOWA01OPEN | KOW 34.5KV BREAKER 252-1 OPEN | 1 | 100001 | BKR_A01_OPEN | BKR_A01_OPEN
KOWA01CONNECT | KOW 34.5KV BREAKER 252-1 POSITION - CONNECTED | 2 | 100002
KOWA01TEST | KOW 34.5KV BREAKER 252-1 POSITION - TEST | 3 | 100003 | BKR_A01_TEST_POS | BKR_A01_TEST_POS
KOWA01DISCONNECT | KOW 34.5KV BREAKER 252-1 POSITION - DISCONNECTED | 4 | 100004 | BKR_A01_DISCONNECT_POSITION | BKR_A01_DISCONNECT_POSITION
KOWA01OCTRIPPED | KOW 34.5KV BREAKER 252-1 IPR OVERCURRENT TRIPPED | 5 | 100005 | BKR_A01_MUXED_OC_TRIP | BKR_A01_MUXED_OC_TRIP
KOWA02CLSD | KOW 34.5KV BREAKER 252-2 CLOSED | 6 | 100006 | BKR_A02_CLOSED | BKR_A02_CLOSED
KOWA02OPEN | KOW 34.5KV BREAKER 252-2 OPEN | 7 | 100007 | BKR_A02_OPEN | BKR_A02_OPEN
KOWA02CONNECT | KOW 34.5KV BREAKER 252-2 POSITION - CONNECTED | 8 | 100008
KOWA02TEST | KOW 34.5KV BREAKER 252-2 POSITION - TEST | 9 | 100009 | BKR_A02_TEST_POS | BKR_A02_TEST_POS
KOWA02DISCONNECT | KOW 34.5KV BREAKER 252-2 POSITION - DISCONNECTED | 10 | 100010 | BKR_A02_DISCONNECT_POSITION | BKR_A02_DISCONNECT_POSITION
KOWA02OCTRIPPED | KOW 34.5KV BREAKER 252-2 IPR OVERCURRENT TRIPPED | 11 | 100011 | BKR_A02_MUXED_OC_TRIP | BKR_A02_MUXED_OC_TRIP
KOW243LOCAL | KOW 34.5KV SWITCHGEAR IN LOCAL CONTROL - L243 | 12 | 100012 | HS_243_LOCAL | HS_243_LOCAL
KOW243REMOTE | KOW 34.5KV SWITCHGEAR IN REMOTE CONTROL - R243 | 13 | 100013
KOW143LOCAL | KOW 1000VDC SWITCGEAR IN LOCAL CONTROL - L143 | 14 | 100014 | HS_143_LOCAL | HS_143_LOCAL
KOW143REMOTE | KOW 1000VDC SWITCHGEAR IN REMOTE CONTROL - R143 | 15 | 100015
KOW186LOCKOUT | KOW 186 LOCKOUT RELAY ACTIVATED | 16 | 100016 | HS_186_TRIP | HS_186_TRIP
KOW286LOCKOUT | KOW 286 LOCKOUT RELAY ACTIVATED | 17 | 100017 | HS_286_TRIP | HS_286_TRIP
KOWX01WTALARM | KOW TRANSFORMER X01 WINDING HIGH TEMP ALARM | 18 | 100018 | X01_226WT_HI_ALM | X01_226WT_HI_ALM
KOWX01WTTRIP | KOW TRANSFORMER X01 WINDING HIGH TEMP TRIP | 19 | 100019 | X01_226WT_HI_TRP | X01_226WT_HI_TRP
KOWX01SPALARM | KOW TRANSFORMER X01 SUDDEN PRESSURE ALARM | 20 | 100020 | X01_263SP_ALM | X01_263SP_ALM
KOWX01SPTRIP | KOW TRANSFORMER X01 SUDDEN PRESSURE TRIP | 21 | 100021 | X01_263SP_TRP | X01_263SP_TRP
KOWX01QTALARM | KOW TRANSFORMER X01 OIL TEMP HIGH ALARM | 22 | 100022 | X01_226QT_ALM | X01_226QT_ALM
KOWX01QTTRIP | KOW TRANSFORMER X01 OIL TEMP HIGH TRIP | 23 | 100023 | X01_226QT_TRP | X01_226QT_TRP
KOWX01OLALARM | KOW TRANSFORMER X01 LOW OIL LEVEL ALARM ALARM | 24 | 100024 | X01_263OL_ALM | X01_263OL_ALM
KOWX01PRVALARM | KOW TRANSFORMER X01 RELIEF DEVICE ALARM | 25 | 100025 | X01_PRV_ALM | X01_PRV_ALM
KOWZ01DOOROPEN | KOW RECTIFIER Z01 DOOR OPEN | 26 | 100026 | Z01_33_DOOR_OPEN_TRP | Z01_33_DOOR_OPEN_TRP
KOWZ01NDSOPEN | KOW RECTIFIER NEGATIVE DISCONNECT SWITCH OPEN | 27 | 100027 | Z01_189_NDS_OPEN | Z01_189_NDS_OPEN
KOWZ01DTHIGHALARM | KOW RECTIFIER DIODE Z01 HIGH TEMP | 28 | 100028 | Z01_126DT_HI_ALM | Z01_126DT_HI_ALM
KOWZ01DCVOLTALARM | KOW CONTROL POWER TROUBLE - TRANSFORMER RECTIFIER UNIT 1 | 29 | 100029 | Z01_27_ALM | Z01_27_ALM
KOWZ01180AXALARM | KOW RECTIFIER DIODE Z01 ALARM | 30 | 100030 | Z01_180AX_ALM | Z01_180AX_ALM
KOWZ01180AXTRIP | KOW RECTIFIER DIODE Z01 TRIP | 31 | 100031 | Z01_180TX_TRP | Z01_180TX_TRP
KOWZ01103AALARM | KOW RECTIFIER Z01 AC SURGE SUPPRESSOR FAILURE | 32 | 100032 | Z01_103ASS_ALM | Z01_103ASS_ALM
KOWZ01103DALARM | KOW RECTIFIER Z01 DC SURGE SUPPRESSOR FAILURE | 33 | 100033 | Z01_103DSS_ALM | Z01_103DSS_ALM
KOWZ01DTHIGHTRIP | KOW RECTIFIER DIODE Z01 HIGH TEMP | 34 | 100034 | Z01_126DT_HI_TRP | Z01_126DT_HI_TRP
KOWZ0127GR1PSALARM | KOW RECTIFIER GND FAULT CIRCUIT CONTROL POWER FAILURE | 35 | 100035 | Z01_27GR1_PS_ALM | Z01_27GR1_PS_ALM
KOWZ01164GENCLGROUNDED | KOW RECTIFIER Z01 ENCLOSURES GROUNDED | 36 | 100036 | Z01_164G_ENCL_GND_ALM | Z01_164G_ENCL_GND_ALM
KOWZ01164AENCLALIVE | KOW RECTIFIER Z01 ENCLOSURES ALIVE | 37 | 100037 | Z01_164A_ENCL_ALIVE_TRP | Z01_164A_ENCL_ALIVE_TRP
KOWX02WTALARM | KOW TRANSFORMER X02 WINDING HIGH TEMP ALARM | 38 | 100038 | X02_226WT_HI_ALM | X02_226WT_HI_ALM
KOWX02WTTRIP | KOW TRANSFORMER X02 WINDING HIGH TEMP TRIP | 39 | 100039 | X02_226WT_HI_TRP | X02_226WT_HI_TRP
KOWX02SPALARM | KOW TRANSFORMER X02 SUDDEN PRESSURE ALARM | 40 | 100040 | X02_263SP_ALM | X02_263SP_ALM
KOWX02SPTRIP | KOW TRANSFORMER X02 SUDDEN PRESSURE TRIP | 41 | 100041 | X02_263SP_TRP | X02_263SP_TRP
KOWX02QTALARM | KOW TRANSFORMER X02 OIL TEMP HIGH ALARM | 42 | 100042 | X02_226QT_ALM | X02_226QT_ALM
KOWX02QTTRIP | KOW TRANSFORMER X02 OIL TEMP HIGH TRIP | 43 | 100043 | X02_226QT_TRP | X02_226QT_TRP
KOWX02OLALARM | KOW TRANSFORMER X02 LOW OIL LEVEL ALARM | 44 | 100044 | X02_263OL_ALM | X02_263OL_ALM
KOWX02PRVALARM | KOW TRANSFORMER X02 RELIEF DEVICE ALARM | 45 | 100045 | X02_PRV_ALM | X02_PRV_ALM
KOWZ02DOOROPEN | KOW RECTIFIER Z02 DOOR OPEN | 46 | 100046 | Z02_33_DOOR_OPEN_TRP | Z02_33_DOOR_OPEN_TRP
KOWZ02NDSOPEN | KOW RECTIFIER NEGATIVE DISCONNECT SWITCH OPEN | 47 | 100047 | Z02_189_NDS_OPEN | Z02_189_NDS_OPEN
KOWZ02DTHIGHALARM | KOW RECTIFIER DIODE Z02 HIGH TEMP | 48 | 100048 | Z02_126DT_HI_ALM | Z02_126DT_HI_ALM
KOWZ02DCVOLTALARM | KOW CONTROL POWER TROUBLE - TRANSFORMER RECTIFIER UNIT 2 | 49 | 100049 | Z02_27_ALM | Z02_27_ALM
KOWZ02180AXALARM | KOW RECTIFIER DIODE Z02 ALARM | 50 | 100050 | Z02_180AX_ALM | Z02_180AX_ALM
KOWZ02180AXTRIP | KOW RECTIFIER DIODE Z02 TRIP | 51 | 100051 | Z02_180TX_TRP | Z02_180TX_TRP
KOWZ02103AALARM | KOW RECTIFIER Z02 AC SURGE SUPPRESSOR FAILURE | 52 | 100052 | Z02_103ASS_ALM | Z02_103ASS_ALM
KOWZ02103DALARM | KOW RECTIFIER Z02 DC SURGE SUPPRESSOR FAILURE | 53 | 100053 | Z02_103DSS_ALM | Z02_103DSS_ALM
KOWZ02DTHIGHTRIP | KOW RECTIFIER DIODE Z02 HIGH TEMP | 54 | 100054 | Z02_126DT_HI_TRP | Z02_126DT_HI_TRP
KOWZ0227GR1PSALARM | KOW RECTIFIER GND FAULT CIRCUIT CONTROL POWER FAILURE | 55 | 100055 | Z02_27GR1_PS_ALM | Z02_27GR1_PS_ALM
KOWZ02164GENCLGROUNDED | KOW RECTIFIER Z02 ENCLOSURES GROUNDED | 56 | 100056 | Z02_164G_ENCL_GND_ALM | Z02_164G_ENCL_GND_ALM
KOWZ02164AENCLALIVE | KOW RECTIFIER Z02 ENCLOSURES ALIVE | 57 | 100057 | Z02_164A_ENCL_ALIVE_TRP | Z02_164A_ENCL_ALIVE_TRP
KOWNGDHIGHCURRENT | KOW G01-1 HIGH CURRENT | 58 | 100058 | NGD_HI_CURRENT_SCR_ALM | NGD_HI_CURRENT_SCR_ALM
KOWNGDTIMEDCURRENT | KOW G01-2 TIMED CURRENT | 59 | 100059 | NGD_TIMED_CURRENT_SCR_ALM | NGD_TIMED_CURRENT_SCR_ALM
KOWNGDBYPASSSWITCHCLOSED | KOW G01-3 BYPASS SWITCH CLOSED | 60 | 100060 | NGD_MODBUS.MAN_BYPASS_SW_OPEN | NGD_MODBUS.MAN_BYPASS_SW_OPEN
KOWNGDFAULT | KOW G01 SYSTEM TROUBLE | 61 | 100061 | NGD_TROUBLE | NGD_TROUBLE
KOWDCENCLALIVE | KOW DC SWITCHGEAR ENCLOSURES ALIVE | 62 | 100062 | DC_ENCLR_ALIVE | DC_ENCLR_ALIVE
KOWDCENCLGROUNDED | KOW DC SWITCHGEAR ENCLOSURES GROUNDED | 63 | 100063 | DC_ENCLR_GND | DC_ENCLR_GND
KOWGNDCKTPOWERFAIL | LOSS OF 125VDC AT ENCLOSURE GROUND PROTECTION CKT. | 64 | 100064 | GND_CKT_PWR_FAIL | GND_CKT_PWR_FAIL
KOWMAINBKRB01CLOSED | KOW 1000VDC MAIN BREAKER 172-1 CLOSED | 65 | 100065 | BKR_B01_CLOSED | BKR_B01_CLOSED
KOWMAINBKRB01OPEN | KOW 1000VDC MAIN BREAKER 172-1 OPEN | 66 | 100066 | BKR_B01_OPEN | BKR_B01_OPEN
KOWMAINBKRB01CONNECTED | KOW 1000VDC MAIN BREAKER 172-1 POSITION - CONNECTED | 67 | 100067
KOWMAINBKRB01TEST | KOW 1000VDC MAIN BREAKER 172-1 POSITION - TEST | 68 | 100068 | BKR_B01_TEST | BKR_B01_TEST
KOWMAINBKRB01DISCONNECTED | KOW 1000VDC MAIN BREAKER 172-1 POSITION - DISCONNECTED | 69 | 100069 | BKR_B01_DISCONNECT_POSITION | BKR_B01_DISCONNECT_POSITION
KOWMAINBKRB04CLOSED | KOW 1000VDC MAIN BREAKER 172-4 CLOSED | 70 | 100070 | BKR_B04_CLOSED | BKR_B04_CLOSED
KOWMAINBKRB04OPEN | KOW 1000VDC MAIN BREAKER 172-4 OPEN | 71 | 100071 | BKR_B04_OPEN | BKR_B04_OPEN
KOWMAINBKRB04CONNECTED | KOW 1000VDC MAIN BREAKER 172-4 POSITION - CONNECTED | 72 | 100072
KOWMAINBKRB04TEST | KOW 1000VDC MAIN BREAKER 172-4 POSITION - TEST | 73 | 100073 | BKR_B04_TEST | BKR_B04_TEST
KOWMAINBKRB04DISCONNECTED | KOW 1000VDC MAIN BREAKER 172-4 POSITION - DISCONNECTED | 74 | 100074 | BKR_B04_DISCONNECT_POSITION | BKR_B04_DISCONNECT_POSITION
KOWFEEDERBKRB02CLOSED | KOW 1000VDC FEEDER BREAKER 172-2 CLOSED | 75 | 100075 | BKR_B02_CLOSED | BKR_B02_CLOSED
KOWFEEDERBKRB02OPEN | KOW 1000VDC FEEDER BREAKER 172-2 OPEN | 76 | 100076 | BKR_B02_OPEN | BKR_B02_OPEN
KOWFEEDERBKRB02CONNECTED | KOW 1000VDC FEEDER BREAKER 172-2 POSITION - CONNECTED | 77 | 100077
KOWFEEDERBKRB02TEST | KOW 1000VDC FEEDER BREAKER 172-2 POSITION - TEST | 78 | 100078 | MPR_B02_MODBUS.BRK_TEST_POSITION | MPR_B02_MODBUS.BRK_TEST_POSITION
KOWFEEDERBKRB02DISCONNECTED | KOW 1000VDC FEEDER BREAKER 172-2 POSITION - DISCONNECTED | 79 | 100079 | MPR_B02_DISCONNECT_POSITION | MPR_B02_DISCONNECT_POSITION
KOWBKRB02MPRTROUBLE | KOW 1000VDC FEEDER BREAKER 172-2 MPR TROUBLE (NC) | 80 | 100080 | MPR_B02_TROUBLE | MPR_B02_TROUBLE
|  | 81 | 100081
KOWBKR02AUTORECLOSELOCKOUT | KOW 1000VDC FEEDER BREAKER 172-2 MPR AUTO-RECLOSE LOCKOUT | 82 | 100082 | MPR_B02_MODBUS.MOD_LED_LOCK_OUT | MPR_B02_MODBUS.MOD_LED_LOCK_OUT
KOWBKR02HARDLOCKOUT | KOW 1000VDC FEEDER BREAKER 172-2 MPR HARD LOCKOUT | 83 | 100083 | MPR_B02_MODBUS.HARD_LOCKOUT | MPR_B02_MODBUS.HARD_LOCKOUT
KOWBKR02MPROCTRIP | KOW 1000VDC FEEDER BREAKER 172-2 POSITION - MPR O/C TRIP | 84 | 100084 | MPR_B02_OVERCURRENT | MPR_B02_OVERCURRENT
KOWFEEDERBKRB03CLOSED | KOW 1000VDC FEEDER BREAKER 172-3 CLOSED | 85 | 100085 | BKR_B03_CLOSED | BKR_B03_CLOSED
KOWFEEDERBKRB03OPEN | KOW 1000VDC FEEDER BREAKER 172-3 OPEN | 86 | 100086 | BKR_B03_OPEN | BKR_B03_OPEN
KOWFEEDERBKRB03CONNECTED | KOW 1000VDC FEEDER BREAKER 172-3 POSITION - CONNECTED | 87 | 100087
KOWFEEDERBKRB03TEST | KOW 1000VDC FEEDER BREAKER 172-3 POSITION - TEST | 88 | 100088 | MPR_B03_MODBUS.BRK_TEST_POSITION | MPR_B03_MODBUS.BRK_TEST_POSITION
KOWFEEDERBKRB03DISCONNECTED | KOW 1000VDC FEEDER BREAKER 172-3 POSITION - DISCONNECTED | 89 | 100089 | MPR_B03_DISCONNECT_POSITION | MPR_B03_DISCONNECT_POSITION
KOWBKRB03MPRTROUBLE | KOW 1000VDC FEEDER BREAKER 172-3 MPR TROUBLE (NC) | 90 | 100090 | MPR_B03_TROUBLE | MPR_B03_TROUBLE
|  | 91 | 100091
KOWBKR03AUTORECLOSELOCKOUT | KOW 1000VDC FEEDER BREAKER 172-3 MPR AUTO-RECLOSE LOCKOUT | 92 | 100092 | MPR_B03_MODBUS.MOD_LED_LOCK_OUT | MPR_B03_MODBUS.MOD_LED_LOCK_OUT
KOWBKR03HARDLOCKOUT | KOW 1000VDC FEEDER BREAKER 172-3 MPR HARD LOCKOUT | 93 | 100093 | MPR_B03_MODBUS.HARD_LOCKOUT | MPR_B03_MODBUS.HARD_LOCKOUT
KOWBKR03MPROCTRIP | KOW 1000VDC FEEDER BREAKER 172-3 POSITION - MPR O/C TRIP | 94 | 100094 | MPR_B03_OVERCURRENT | MPR_B03_OVERCURRENT
KOWCONTACTRAILKL01DEENERGISED | KOW CONTACT RAIL SECTION (KL01) DE-ENERGIZED (MPR) | 95 | 100095 | MPR_B02_MODBUS.UNDERVOLTAGE | MPR_B02_MODBUS.UNDERVOLTAGE
KOWCONTACTRAILAR04DEENERGISED | KOW CONTACT RAIL SECTION (AR04) DE-ENERGIZED (MPR) | 96 | 100096 | MPR_B03_MODBUS.UNDERVOLTAGE | MPR_B03_MODBUS.UNDERVOLTAGE
KOWIOMC02HS1FAILALARM | KOW 2505 TROUBLE ALARM IOM_C02_HS1 | 97 | 100097 | IOM_C02_HS1_FAIL | IOM_C02_HS1_FAIL
KOWIOMC02HS2FAILALARM | KOW 2505 TROUBLE ALARM IOM_C02_HS2 | 98 | 100098 | IOM_C02_HS2_FAIL | IOM_C02_HS2_FAIL
KOWETTSEQPTFAULT | KOW ETTS EQUIPMENT TROUBLE (HARDWARE) | 99 | 100099 | ETTC_BLS_FAULT | ETTC_BLS_FAULT
KOWETTSCOMMOFFLINE | KOW ETTS COMMUNICATION TROUBLE | 100 | 100100 | ETTC_OFFLINE | ETTC_OFFLINE
KOWETTSPLATFORM2TRIP | KOW ETTS PLATFORM 2 TRIP INDICATION KL01 | 101 | 100101 | ETTC_PT2_KL01 | ETTC_PT2_KL01
KOWETTSPLATFORM1TRIP | KOW ETTS PLATFORM 1 TRIP INDICATION AR04 | 102 | 100102 | ETTC_PT1_AR04 | ETTC_PT1_AR04
KOWETTSTRIPRAILZONEKL01 | KOW TRANSFER TRIP RAIL ZONE KL01 | 103 | 100103 | ETTC_MPR_02_TT | ETTC_MPR_02_TT
KOWETTSTRIPRAILZONEAR04 | KOW TRANSFER TRIP RAIL ZONE AR04 | 104 | 100104 | ETTC_MPR_03_TT | ETTC_MPR_03_TT
KOWL0127UNDERVOLTAGEALARM | KOW 120V AC PANEL UNDERVOLTAGE | 105 | 100105 | L01_27_UNDERVOLT | L01_27_UNDERVOLT
KOWBKRA0127UNDERVOLTAGE | KOW H01 CONTROL POWER TROUBLE - 34.5KV SWITCHGEAR | 106 | 100106 | BKR_A01_UNDERVOLT | BKR_A01_UNDERVOLT
KOWBKRA0227UNDERVOLTAGE | KOW H02 CONTROL POWER TROUBLE - 34.5KV SWITCHGEAR | 107 | 100107 | BKR_A02_UNDERVOLT | BKR_A02_UNDERVOLT
KOWBKRB01POWERFAIL | KOW CONTROL POWER TROUBLE - DC SWITCHGEAR 172-1 | 108 | 100108 | BKR_B01_CTRL_PWR_UNDERVOLT | BKR_B01_CTRL_PWR_UNDERVOLT
KOWBKRB04POWERFAIL | KOW CONTROL POWER TROUBLE - DC SWITCHGEAR 172-4 | 109 | 100109 | BKR_B04_CTRL_PWR_UNDERVOLT | BKR_B04_CTRL_PWR_UNDERVOLT
KOWBKRB02POWERFAIL | KOW CONTROL POWER TROUBLE - DC SWITCHGEAR 172-2 | 110 | 100110 | BKR_B02_CTRL_PWR_UNDERVOLT | BKR_B02_CTRL_PWR_UNDERVOLT
KOWBKRB03POWERFAIL | KOW CONTROL POWER TROUBLE - DC SWITCHGEAR 172-3 | 111 | 100111 | BKR_B03_CTRL_PWR_UNDERVOLT | BKR_B03_CTRL_PWR_UNDERVOLT
KOWC02PS1TROUBLE ALARM | KOW DC/DC CONVERTOR PS1 TROUBLE | 112 | 100112 | PS1_24VDC_ALM | PS1_24VDC_ALM
KOWC02PS2TROUBLE ALARM | KOW DC/DC CONVERTOR PS2 TROUBLE | 113 | 100113 | PS2_24VDC_ALM | PS2_24VDC_ALM
|  | 114 | 100114
KOWNETWORKSWITCHTROUBLE | KOW IE-3010 NETWORK SWITCH TROUBLE | 115 | 100115 | IE3010_TROUBLE_ALM | IE3010_TROUBLE_ALM
KOWNETWORKSWITCHHIGHTEMPALARM | KOW CCA NETWORK SWITCH HIGH TEMP ALARM | 116 | 100116 | CCA_IE3000_HI_TEMP | CCA_IE3000_HI_TEMP
KOWNETWORKSWITCHPOWERFAILALARM | KOW CCA NETWORK SWITCH POWER SUPPLY ALARM | 117 | 100117 | CCA_IE3000_PWR_TROUBLE | CCA_IE3000_PWR_TROUBLE
KOWBATTERYVOLTAGEPROBLEM | KOW BATTERY SYSTEM VOLTAGE PROBLEM | 118 | 100118 | BC01_BATT_VOLT_PROB_ALARM | BC01_BATT_VOLT_PROB_ALARM
KOWBATTERYCHARGEROVERLOAD | KOW BATTERY CHARGER OVERLOAD | 119 | 100119 | BC01_BATT_C_OVERLOAD_ALARM | BC01_BATT_C_OVERLOAD_ALARM
KOWBATTERYHIGHTEMPALARM | KOW BATTERY HIGH TEMPERATURE | 120 | 100120 | BC01_BATT_OVERTMP_SWITCH | BC01_BATT_OVERTMP_SWITCH
KOWBATTERYFANFAILALARM | KOW LOSS OF BATTERY AIR FLOW | 121 | 100121 | BC01_BATT_FAN_AIRFLOW_LOSS_ALM | BC01_BATT_FAN_AIRFLOW_LOSS_ALM
KOWFIREALARMPANELSUMMARYALARM | KOW FIRE ALARM SUMMARY ALARM | 122 | 100122 | FIRE_ALM_PANEL_ALARM | FIRE_ALM_PANEL_ALARM
KOWFIREALARMPANELTROUBLE | KOW FIRE ALARM PANEL TROUBLE | 123 | 100123 | FIRE_ALM_PANEL_TROUBLE | FIRE_ALM_PANEL_TROUBLE
KOWRHOUSE2VENTFAILALARM | KOW LOSS OF RECTIFIER HOUSE 2 VENTLATION | 124 | 100124 | DC_HOUSE2_HVAC_PWR_FAIL | DC_HOUSE2_HVAC_PWR_FAIL
KOWDCHOUSE1VENTFAILALARM | KOW LOSS OF DC SWITCHGEAR HOUSE 1 VENTLATION | 125 | 100125 | DC_HOUSE_HVAC_PWR_FAIL | DC_HOUSE_HVAC_PWR_FAIL
KOWHOUSE2HIGHTEMPALARM | KOW HOUSE 2 HIGH TEMP | 126 | 100126 | DC_HOUSE2_HIGH_TMP_ALM | DC_HOUSE2_HIGH_TMP_ALM
KOWHOUSE1HIGHTEMPALARM | KOW HOUSE 1 HIGH TEMP | 127 | 100127 | DC_HOUSE_HIGH_TMP_ALM | DC_HOUSE_HIGH_TMP_ALM
KOWBKR252_1UNCOMMANDED | KOW 34.5KV SECONDARY BREAKER 252-1_UNCOMMANDED_CHANGE_OF_STATE |  | 100152 |  | BKR_A01_UNCMD
KOWBKR252_1COMMANDFAIL | KOW 34.5KV SECONDARY BREAKER 252-1_INCOMPLETE_SEQUENCE |  | 100153 |  | BKR_A01_CMD_FAIL
KOWBKR252_2UNCOMMANDED | KOW 34.5KV PRIMARY BREAKER 252-2_UNCOMMANDED_CHANGE_OF_STATE |  | 100154 |  | BKR_A02_UNCMD
KOWBKR252_2COMMANDFAIL | KOW 34.5KV PRIMARY BREAKER 252-2_INCOMPLETE_SEQUENCE |  | 100155 |  | BKR_A02_CMD_FAIL
KOWBKR172_1UNCOMMANDED | KOW_1000VDC_FEEDER_BREAKER_172_1_UNCOMMANDED_CHANGE_OF_STATE |  | 100156 |  | BKR_B01_UNCMD
KOWBKR172_1COMMANDFAIL | KOW_1000VDC_FEEDER_BREAKER_172_1_INCOMPLETE_SEQUENCE |  | 100157 |  | BKR_B01_CMD_FAIL
KOWBKR172_2UNCOMMANDED | KOW_1000VDC_FEEDER_BREAKER_172_2_UNCOMMANDED_CHANGE_OF_STATE |  | 100158 |  | BKR_B02_UNCMD
KOWBKR172_2COMMANDFAIL | KOW_1000VDC_FEEDER_BREAKER_172_2_INCOMPLETE_SEQUENCE |  | 100159 |  | BKR_B02_CMD_FAIL
KOWBKR172_3UNCOMMANDED | KOW_1000VDC_FEEDER_BREAKER_172_3_UNCOMMANDED_CHANGE_OF_STATE |  | 100160 |  | BKR_B03_UNCMD
KOWBKR172_3COMMANDFAIL | KOW_1000VDC_FEEDER_BREAKER_172_3_INCOMPLETE_SEQUENCE |  | 100161 |  | BKR_B03_CMD_FAIL
KOWBKR172_4UNCOMMANDED | KOW_1000VDC_FEEDER_BREAKER_172_4_UNCOMMANDED_CHANGE_OF_STATE |  | 100162 |  | BKR_B04_UNCMD
KOWBKR172_4COMMANDFAIL | KOW_1000VDC_FEEDER_BREAKER_172_4_INCOMPLETE_SEQUENCE |  | 100163 |  | BKR_B04_CMD_FAIL
KOW_BLS_TRIP | KOW BLUE LIGHT STATION TRIP | 164 | 100164 | ETTC_BLS_TRIP | ETTC_BLS_TRIP
KOW_B01_DIR_PWR_TRIP | KOW BKR 172-1 REVERSE CURRENT TRIP | 165 | 100165 | BKR_B01_DIR_PWR_TRP | BKR_B01_DIR_PWR_TRP
KOW_B04_DIR_PWR_TRIP | KOW BKR 172-4 REVERSE CURRENT TRIP | 166 | 100166 | BKR_B04_DIR_PWR_TRP | BKR_B04_DIR_PWR_TRP
ETTC_CHNLA_OUTAGE1 | ETTC SERIAL CHANNEL A COMMUNICATION TROUBLE | 167 | 100167 | ETTC_CHNLA_OUTAGE1 | ETTC_CHNLA_OUTAGE1
ETTC_CHNLB_OUTAGE1 | ETTC SERIAL CHANNEL B COMMUNICATION TROUBLE | 168 | 100168 | ETTC_CHNLB_OUTAGE1 | ETTC_CHNLB_OUTAGE1
A01_OFFLINE | AC BKR 252-1 OFFLINE | 171 | 100171 | A01_OFFLINE | A01_OFFLINE
A02_OFFLINE | AC BKR 252-2 OFFLINE | 172 | 100172 | A02_OFFLINE | A02_OFFLINE
X01_OFFLINE | TRANSFORMER X01 OFFLINE | 173 | 100173 | X01_OFFLINE | X01_OFFLINE
X02_OFFLINE | TRANSFORMER X02 OFFLINE | 174 | 100174 | X02_OFFLINE | X02_OFFLINE
Z01_OFFLINE | RECTIFIER Z01 OFFLINE | 175 | 100175 | Z01_OFFLINE | Z01_OFFLINE
Z02_OFFLINE | RECTIFIER Z02 OFFLINE | 176 | 100176 | Z02_OFFLINE | Z02_OFFLINE
MPR_B02_OFFLINE | DC FDR BKR MPR_B02 OFFLINE | 177 | 100177 | MPR_B02_OFFLINE | MPR_B02_OFFLINE
MPR_B03_OFFLINE | DC FDR BKR MPR_B03 OFFLINE | 178 | 100178 | MPR_B03_OFFLINE | MPR_B03_OFFLINE
NGD_OFFLINE | NGD DEVICE OFFLINE | 179 | 100179 | NGD_OFFLINE | NGD_OFFLINE
IOM_DC_OFFLINE | IOM_DC OFFLINE | 180 | 100180 | IOM_DC_OFFLINE | IOM_DC_OFFLINE
BATT_CHARGER_OFFLINE | BATTERY CHARGER OFFLINE | 181 | 100181 | BATT_CHARGER_OFFLINE | BATT_CHARGER_OFFLINE
ETTC_IOM_ETP_ALARM | ETTC 2505 IOM-ETP COMMUNICATION TROUBLE | 182 | 100182 | ETTC_IOM_ETP_ALARM | ETTC_IOM_ETP_ALARM
ETTC_IOM_TRP_ALARM | ETTC 2505 IOM-TRP COMMUNICATION TROUBLE | 183 | 100183 | ETTC_IOM_TRP_ALARM | ETTC_IOM_TRP_ALARM

## Sheet1
HMI_SRVR_MODBUS.HREG_00016.status.stVal.00 | Tags.A01_OFFLINE | EBP_SRVR_MODBUS.DI_00170
HMI_SRVR_MODBUS.HREG_00016.status.stVal.01 | Tags.A02_OFFLINE | EBP_SRVR_MODBUS.DI_00171 | Tags.A01_OFFLINE | ICS_SRVR_MAP_DNP.BI_00171
HMI_SRVR_MODBUS.HREG_00016.status.stVal.02 | Tags.X01_OFFLINE | EBP_SRVR_MODBUS.DI_00172 | Tags.A02_OFFLINE | ICS_SRVR_MAP_DNP.BI_00172
HMI_SRVR_MODBUS.HREG_00016.status.stVal.03 | Tags.X02_OFFLINE | EBP_SRVR_MODBUS.DI_00173 | Tags.X01_OFFLINE | ICS_SRVR_MAP_DNP.BI_00173
HMI_SRVR_MODBUS.HREG_00016.status.stVal.04 | Tags.Z01_OFFLINE | EBP_SRVR_MODBUS.DI_00174 | Tags.X02_OFFLINE | ICS_SRVR_MAP_DNP.BI_00174
HMI_SRVR_MODBUS.HREG_00016.status.stVal.05 | Tags.Z02_OFFLINE | EBP_SRVR_MODBUS.DI_00175 | Tags.Z01_OFFLINE | ICS_SRVR_MAP_DNP.BI_00175
HMI_SRVR_MODBUS.HREG_00016.status.stVal.06 | Tags.MPR_B02_OFFLINE | EBP_SRVR_MODBUS.DI_00176 | Tags.Z02_OFFLINE | ICS_SRVR_MAP_DNP.BI_00176
HMI_SRVR_MODBUS.HREG_00016.status.stVal.07 | Tags.MPR_B03_OFFLINE | EBP_SRVR_MODBUS.DI_00177 | Tags.MPR_B02_OFFLINE | ICS_SRVR_MAP_DNP.BI_00177
HMI_SRVR_MODBUS.HREG_00016.status.stVal.08 | Tags.NGD_OFFLINE | EBP_SRVR_MODBUS.DI_00178 | Tags.MPR_B03_OFFLINE | ICS_SRVR_MAP_DNP.BI_00178
HMI_SRVR_MODBUS.HREG_00016.status.stVal.09 | Tags.IOM_DC_OFFLINE | EBP_SRVR_MODBUS.DI_00179 | Tags.NGD_OFFLINE | ICS_SRVR_MAP_DNP.BI_00179
HMI_SRVR_MODBUS.HREG_00016.status.stVal.10 | Tags.BATT_CHARGER_OFFLINE | EBP_SRVR_MODBUS.DI_00180 | Tags.IOM_DC_OFFLINE | ICS_SRVR_MAP_DNP.BI_00180
HMI_SRVR_MODBUS.HREG_00016.status.stVal.11 |  | EBP_SRVR_MODBUS.DI_00181 | Tags.BATT_CHARGER_OFFLINE | ICS_SRVR_MAP_DNP.BI_00181
HMI_SRVR_MODBUS.HREG_00016.status.stVal.12 |  | EBP_SRVR_MODBUS.DI_00182
HMI_SRVR_MODBUS.HREG_00016.status.stVal.13 |  | EBP_SRVR_MODBUS.DI_00183
HMI_SRVR_MODBUS.HREG_00016.status.stVal.14 |  | EBP_SRVR_MODBUS.DI_00184
HMI_SRVR_MODBUS.HREG_00016.status.stVal.15